Sample Specifications Steam

Model CBEX Premium 100-800 HP

GENERAL

Boiler Characteristics (Steam) - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 22

PRODUCTS

General Boiler Design  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 22

Steam Boiler Trim	- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 23

Burner  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 24

Fuel Specification And Piping - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 24

Uncontrolled NOx - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 24

30 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 29

9 PPM - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 35

Boiler Controls And Control Panel  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 41

Flue Gas Heat Recovery (Optional Selection) - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 42

Efficiency Guarantee - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 42

EXECUTION

Warranty - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 42

Shop Tests  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 42

SAMPLE SPECIFICATIONS

The following sample specifications are provided by Cleaver-Brooks to assist you in meeting your customer's specific needs and application.

The Sample Specifications are typically utilized as the base template for the complete boiler specification. Contact your local Cleaver-Brooks authorized representative for information on special insurance requirements, special code requirements, optional equipment, or general assistance in completing the specification.

PART 1 	GENERAL

CBEX Steam Boiler 100-800 HP

1.1	BOILER CHARACTERISTICS (STEAM)

A.	The Steam Boiler shall be Cleaver-Brooks Fuel Series

(100, 200, 700),	hp

designed for

psig (150, 200, or 250 psig steam). The maximum operating pressure

shall be

psig and the minimum operating pressure shall be

psig (note - minimum

allowable operating pressure on the CBEX is 50 psig).

B.	The boiler shall have a maximum output of

Btu/hr, or

horsepower when fired

with CS12-48 #2 oil and/or natural gas,

Btu/cu-ft. Electrical power available shall be

PART 2 	PRODUCTS

Volt

Phase

Cycle.

2.1	GENERAL BOILER DESIGN

A.	Design shall be optimized using CFD modeling verifiable by manufacturer. The boiler shall be a multipass pass horizontal firetube updraft boiler with extended heating surface optimized to reduce boiler foot print. Boiler shall be mounted on a heavy steel frame with forced draft burner of gun design.

1.	The boiler shall be completely preassembled and fire tested at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.

2.	The boiler shall be built to comply with the following insurance and codes  (Factory

Mutual, XL GAP, ASME, NFPA 8501).

B.	Boiler Shell (Steam)

1.	The boiler shell must be constructed in accordance with ASME Boiler Code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.

2.	The boiler shall be furnished with a manhole and handholes to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.

3.	The front smokebox doors shall be davited and sealed with superwool insulation and fastened tightly using locking lugs on steel studs.

4.	The rear door shall be fitted with an access plug for rear fireside inspection.

5.	The boiler tubes shall not include turbulators, swirlers, or other add-on appurtenances.

6.	The exhaust gas vent shall be located at the front of the boiler and be capable of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.

7.	Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.

8.	The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled if required.

9.	The entire boiler base frame and other components shall be factory painted before shipment, using a hard-finish enamel coating.

10.  The boiler shall contain a chemical feed connection.

2.2	STEAM BOILER TRIM

A.	Water Column: A water column shall be located on the right hand side of the boiler complete with gauge glass set and water column blowdown valves.

1.	Feedwater Pump Control

The boiler feedwater pump control shall be included as an integral part of the water

column to automatically actuate a motor driven feedwater pump maintaining the boiler

water level within normal limits.

2.	Low Water Cutoff

The low water cutoff shall be included as an integral part of the boiler feedwater control

wired into the burner control circuit to prevent burner operation if the boiler water level

falls below a safe level.

B.	Auxiliary Low Water Cut-off

Auxiliary low water cut-off shall be included, piped to the vessel, and wired to the burner

control circuit. A manual reset device shall be used on this control.

C.	Steam Pressure Gauge

The steam pressure gauge shall be located at the front of the boiler and include cock and test

connection.

D.	Safety Valves

Safety valves of a type and size to comply with ASME Code requirements shall be shipped

loose.

E.	Steam Pressure Controls

The steam pressure control to regulate burner operation shall be mounted near the water

column. Controls shall be a high limit (manual reset), operating limit (auto reset), and firing rate

control.

2.3	BURNER

A.	Burner shall incorporate Cleaver Brooks “Lean Burn Technology”.

B.	Fuel and air ratio/mixture shall be controlled over the entire operating range, allowing for firing at constant excess air on high turndown burner application.

C.	Burner to be designed specifically for boiler including optimized furnace allowing for low emissions and lean burn combustion.

D.	Mode of Operation

1.	Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.

2.	A low fire hold temperature control is mounted and wired on the boiler. E.	Blower

1.	Air for combustion shall be supplied by a forced draft blower incorporated into the burner design to eliminate vibration and reduce noise level.

2.	Maximum sound level of the boiler/burner package shall not exceed measured in accordance with ABMA Sound Test Standards).

dbA (when

3.	The impeller shall be fabricated aluminum with radial blade, carefully balanced, and directly connected to the blower motor shaft.

F.	Combustion Air Control

Combustion air damper and fuel metering valve shall be operated by individual actuators to

regulate the flame according to load demand.

2.4	FUEL SPECIFICATION AND PIPING

Select one of the following fuel types:

• Fuel series 700 - Gas-fired.

• Fuel series 100 - Light oil (No. 2) fired .

• Fuel series 200 - Light oil or gas-fired.

NOTE: Specification writer to select between NOx options of Uncontrolled, 30 ppm, or 9 ppm NOx on Natural Gas as required for specific project conditions.

Uncontrolled NOx Operation Natural Gas

CBEX 100 to 200 Horsepower Uncontrolled NOx

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm at 50, 75 and 100 % of firing and 25 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |

2.	Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided.

4.	Oil Burner Piping

a.	Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit.

5.	Fuel oil is pressure atomized.

6.	Turndown range shall be 4:1 when firing No. 2 oil.

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 4:1 when firing natural gas. |

c.	CO on Natural Gas is 10 ppm at 50, 75 and 100 % of firing and 25 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate.

CBEX 250 and 300 Horsepower Uncontrolled NOx

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm). |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 7:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test Gconnection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 7:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm). |

CBEX 350 to 800 Horsepower Uncontrolled NOx

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |

|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
| --- | --- | --- |
|  | 4. | Burner Turndown: Turndown range shall be 10:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15 |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 8:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 8:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 10:1 when firing natural gas. c.	CO on Natural Gas is 10 ppm with excess air at 15%.

30 PPM NOx Operation Natural Gas

CBEX 100 to 200 Horsepower 30 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm at 50, 75 and 100 % of firing and 50 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |

| B. | Fue 1. | l Series 100 - Light Oil-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a low |
| --- | --- | --- |
|  |  | pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 4:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High |

and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 4:1 when firing natural gas.

c.	CO on Natural Gas is 25 ppm at 50, 75 and 100 % of firing and 50 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate.

CBEX 250 and 300 Horsepower 30 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm). |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, |

all integrally mounted on the unit.

5.	Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch.

6.	Turndown range shall be 7:1 when firing No. 2 oil.

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | b. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | c. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | d. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | e. Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. |
|  |  | f. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 7:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm. |

CBEX 350 to 800 Horsepower 30 PPM

| A. | Fue | l Series 700 - Gas-Fired |
| --- | --- | --- |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |

|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
| --- | --- | --- |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 10:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 8:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |

3.	Oil Burner

a.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 8:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 10:1 when firing natural gas. c.	CO on Natural Gas is 10 ppm with excess air at 15%.

9 PPM NOx Operation Natural Gas

CBEX 100 to 200 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |

|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
| --- | --- | --- |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 4:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff |

valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 4:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

CBEX 250 to 400 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 5:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil |

metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit.

5.	Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch.

6.	Turndown range shall be 5:1 when firing No. 2 oil.

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 5:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 5:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 25 ppm with excess air at 25%. |

CBEX 500 and 600 Horsepower 9 PPM

A.	Fuel Series 700 - Gas-Fired

1.	Burner type - The burner shall be mounted at the front of the boiler

|  |  | and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
| --- | --- | --- |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 6:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 6:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue | l Series 200 - Light Oil or Gas-Fired |
| --- | --- | --- |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |

2.	Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3.	Oil Burner

a.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 6:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 6:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

CBEX 700 and 800 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |

|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
| --- | --- | --- |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 7:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |
| C. | Fue | l Series 200 - Light Oil or Gas-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test |

connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 7:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

2.5	BOILER CONTROLS AND CONTROL PANEL

A.	Control Panel - shall be integral with the burner and shall contain a flame safeguard control, motor relays, and terminal strips mounted internally on a panel subbase. Lights, switches, and a control circuit breaker are mounted externally.

B.	Entrance Panel - high voltage panel shall be NEMA 4/12 rated and shall be mounted at the side of the boiler in a location convenient to the operator.

C.	CB780E Flame Safeguard - Each boiler shall be factory equipped with flame safeguard controller panel-mounted.

Oil, heat and moisture resistant wire shall be used and identified with circuit numbers corresponding to the electrical wiring diagram.

Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.

2.6	FLUE GAS HEAT RECOVERY (OPTIONAL SELECTION)

A.	Add Cleaver Brooks economizer selection in this area.

B.	Boiler and economizer to be designed with integral supports allowing for easy economizer installation on boiler eliminating the requirement for separate structure steel support.

2.7	EFFICIENCY GUARANTEE

A.	The boiler must be guaranteed to operate at a minimum fuel-to-steam efficiency of

percent at 100% of rating when burning natural gas and

fuel-to-steam efficiency at

100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).

PART 3 	EXECUTION

3.1	WARRANTY

A.	All equipment is to be guaranteed against defects in materials and/or workmanship for a period of 12 months from date of start-up, or 18 months from date of shipment; whichever comes first.

3.2	SHOP TESTS

A.	The packaged boiler must receive factory tests to check the construction, controls, and operation of the unit. All tests may be witnessed by the purchaser, if desired.

B.	Start-up Service

1.	After boiler installation is completed, the manufacturer shall provide the services of a field representative for starting the unit and training the operator at no additional costs.

2.	A factory-approved and authorized start-up report shall be submitted to the customer/user at the time of start-up.

Sample Specifications Hot Water

Model CBEX Premium 100-800 HP

GENERAL

Boiler Characteristics (HW) - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 44

PRODUCTS

General Boiler Design  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 44

Hot Water Boiler Trim - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 45

Burner  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 45

Fuel Specification And Piping - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 45

60 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 46

30 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 51

9 PPM - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 56

Boiler Controls And Control Panel  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 63

Flue Gas Heat Recovery (Optional Selection) - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 63

Efficiency Guarantee - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 63

EXECUTION

Warranty - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 63

Shop Tests  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 63

SAMPLE SPECIFICATIONS

The following sample specifications are provided by Cleaver-Brooks to assist you in meeting your customer's specific needs and application.

The Sample Specifications are typically utilized as the base template for the complete boiler specification. Contact your local Cleaver-Brooks authorized representative for information on special insurance requirements, special code requirements, optional equipment, or general assistance in completing the specification.

PART 1 	GENERAL

CBEX Steam Boiler 100-800 HP

1.1	BOILER CHARACTERISTICS (HOT WATER)

A.	The boiler shall be Cleaver-Brooks Fuel Series

(100, 200, 700),

hp designed for

psig (30, 125, or other psig) hot water. The maximum operating pressure shall be

psig and the minimum operating pressure shall be

psig.

B.	The boiler shall have a maximum output of

Btu/hr, or

horsepower when fired

with CS12-48 #2 oil and/or natural gas,

Btu/cu-ft. Electrical power available shall be

PART 2 	PRODUCTS

Volt

Phase

Cycle.

2.1	GENERAL BOILER DESIGN

A.	Design shall be optimized using CFD modeling verifiable by manufacturer. The boiler shall be a multipass pass horizontal firetube updraft boiler with extended heating surface optimized to reduce boiler foot print. Boiler shall be mounted on a heavy steel frame with forced draft burner of gun design.

1.	The boiler shall be completely preassembled and fire tested at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.

2.	The boiler shall be built to comply with the following insurance and codes (Factory Mutual, XL GAP, ASME, NFPA 8501).

B.	Boiler Shell (Hot Water)

1.	The boiler shell must be constructed in accordance with ASME boiler code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.

2.	The hot water return and outlet connections shall be located on the top center line of the boiler. The boiler shall be designated to rapidly mix the return water with the boiler water. Forced internal circulation shall be used.

3.	A dip tube shall be included as an integral part of the water outlet.

4.	The boiler shall be furnished with a manhole and handholes to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.

5.	The front smokebox doors shall be davited and sealed with superwool insulation and fastened tightly using locking lugs on steel studs.

6.	The rear head shall be fitted with an access plug for rear fireside inspection.

7.	The boiler tubes shall not include turbulators, swirlers, or other add-on appurtenances.

8.	The exhaust gas vent shall be located at the front of the boiler and be capable of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.

9.	Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.

10.  The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled if required.

11.  The entire boiler base frame and other components shall be factory painted before shipment, using a hard-finish enamel coating.

12.  The boiler shall contain a chemical feed connection.

| 2.2 | HO A. | T WATER BOILER TRIM Low Water Cutoff - A low water cutoff control (manual reset) shall be mounted on the top |
| --- | --- | --- |
|  |  | centerline of the boiler wired into the burner control circuit to prevent burner operation if boiler water falls below a safe level. |
|  | B. | Pressure and Temperature Gauges - Pressure and temperature gauges shall be mounted on the boiler with temperature sensing element located adjacent to the hot water outlet. |
|  | C. | Relief Valves - Water relief valves of a type and size to comply with ASME Code requirements shall be shipped loose. |
|  | D. | Temperature Controls - Temperature controls to regulate burner operation shall be mounted on the unit with temperature sensing elements located adjacent to the hot water outlet. Controls shall be high limit (manual reset), operating limit (auto reset), and firing rate control. |

2.3	BURNER

A.	Burner shall incorporate Cleaver Brooks “Lean Burn Technology”.

B.	Fuel and air ratio/mixture shall be controlled over the entire operating range, allowing for firing at constant excess air on high turndown burner application.

C.	Burner to be designed specifically for boiler including optimized furnace allowing for low emissions and lean burn combustion.

D.	Mode of Operation

1.	Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.

2.	A low fire hold temperature control is mounted and wired on the boiler. E.	Blower

1.	Air for combustion shall be supplied by a forced draft blower incorporated into the burner design to eliminate vibration and reduce noise level.

2.	Maximum sound level of the boiler/burner package shall not exceed measured in accordance with ABMA Sound Test Standards).

dbA (when

3.	The impeller shall be fabricated aluminum with radial blade, carefully balanced, and directly connected to the blower motor shaft.

F.	Combustion Air Control

Combustion air damper and fuel metering valve shall be operated by individual actuators to

regulate the flame according to load demand.

2.4	FUEL SPECIFICATION AND PIPING

Select one of the following fuel types:

• Fuel series 700 - Gas-fired.

• Fuel series 100 - Light oil (No. 2) fired .

• Fuel series 200 - Light oil or gas-fired.

NOTE: Specification writer to select between NOx options of Uncontrolled, 30 ppm, or 9 ppm NOx on Natural Gas as required for specific project conditions.

Uncontrolled NOx Operation Natural Gas

CBEX 100 to 200 Horsepower Uncontrolled NOx

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm at 50, 75 and 100 % of firing and 25 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Fuel oil is pressure atomized. |
|  | 6. | Turndown range shall be 4:1 when firing No. 2 oil. |

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 4:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 10 ppm at 50, 75 and 100 % of firing and 25 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |

CBEX 250 and 300 Horsepower Uncontrolled NOx

| A. | Fue | l Series 700 - Gas-Fired |
| --- | --- | --- |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |

|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
| --- | --- | --- |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm). |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 7:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |

3.	Oil Burner

a.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test Gconnection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 7:1 when firing natural gas.

c.	CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm).

CBEX 350 to 800 Horsepower Uncontrolled NOx

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 10:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |

| B. | 5. Fue 1. | CO on Natural Gas is 10 ppm with excess air at 15 l Series 100 - Light Oil-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a low |
| --- | --- | --- |
|  |  | pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 8:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 8:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating |

plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 10:1 when firing natural gas. c.	CO on Natural Gas is 10 ppm with excess air at 15%.

30 PPM NOx Operation Natural Gas

CBEX 100 to 200 Horsepower 30 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm at 50, 75 and 100 % of firing and 50 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering |

controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit.

5.	Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch.

6.	Turndown range shall be 4:1 when firing No. 2 oil.

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 4:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 25 ppm at 50, 75 and 100 % of firing and 50 ppm at 25% firing rate. Excess air is 15% at 50, 75 and 100% of firing and 30% at 25% firing rate. |

CBEX 250 and 300 Horsepower 30 PPM

A.	Fuel Series 700 - Gas-Fired

1.	Burner type - The burner shall be mounted at the front of the boiler and shall be of high

|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
| --- | --- | --- |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm). |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 7:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue | l Series 200 - Light Oil or Gas-Fired |
| --- | --- | --- |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |

2.	Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3.	Oil Burner

b.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

c.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

d.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

e.	Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. f.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 7:1 when firing natural gas.

c.	CO on Natural Gas is 10 ppm with excess air at 15%. Turndown of 10:1 on natural gas can be achieved (however, excess air will increase to 40% with CO at 50 ppm.

CBEX 350 to 800 Horsepower 30 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |

|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
| --- | --- | --- |
|  | 4. | Burner Turndown: Turndown range shall be 10:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 10 ppm with excess air at 15%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 8:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 8:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 10:1 when firing natural gas. c.	CO on Natural Gas is 10 ppm with excess air at 15%.

9 PPM NOx Operation Natural Gas

CBEX 100 to 200 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 4:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |

| B. | Fue 1. | l Series 100 - Light Oil-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a low |
| --- | --- | --- |
|  |  | pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 4:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 4:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff |

valve. An additional plug cock shall be furnished at entrance to

gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 4:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

CBEX 250 to 400 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 5:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |

5.	Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch.

6.	Turndown range shall be 5:1 when firing No. 2 oil.

7.	Excess air is 25% with 10 ppm CO.

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 5:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  |  | b. Burner Turndown - Turndown range shall be 5:1 when firing natural gas. |
|  |  | c. CO on Natural Gas is 25 ppm with excess air at 25%. |

CBEX 500 and 600 Horsepower 9 PPM

| A. | Fue | l Series 700 - Gas-Fired |
| --- | --- | --- |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |

|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
| --- | --- | --- |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 6:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |
| B. | Fue | l Series 100 - Light Oil-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 6:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |

| C. | Fue 1. | l Series 200 - Light Oil or Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a |
| --- | --- | --- |
|  |  | combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |

3.	Oil Burner

a.	Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b.	Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.	Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.	Burner Turndown - Turndown range shall be 6:1 when firing No. 2 oil. e.	Excess air is 25% with 10 ppm CO.

4.	Gas Burner

a.	Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 6:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

CBEX 700 and 800 Horsepower 9 PPM

| A. | Fue 1. | l Series 700 - Gas-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be of high |
| --- | --- | --- |
|  |  | radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option. |
|  | 4. | Burner Turndown: Turndown range shall be 7:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure). |
|  | 5. | CO on Natural Gas is 25 ppm with excess air at 25%. |

| B. | Fue 1. | l Series 100 - Light Oil-Fired Burner type - The burner shall be mounted at the front of the boiler and shall be a low |
| --- | --- | --- |
|  |  | pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided. |
|  | 4. | Oil Burner Piping |
|  |  | a. Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit. |
|  | 5. | Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch. |
|  | 6. | Turndown range shall be 7:1 when firing No. 2 oil. |
|  | 7. | Excess air is 25% with 10 ppm CO. |
| C. | Fue | l Series 200 - Light Oil or Gas-Fired |
|  | 1. | Burner type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas. |
|  | 2. | Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only). |
|  | 3. | Oil Burner |
|  |  | a. Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank. |
|  |  | b. Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit. |
|  |  | c. Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch. |
|  |  | d. Burner Turndown - Turndown range shall be 7:1 when firing No. 2 oil. |
|  |  | e. Excess air is 25% with 10 ppm CO. |
|  | 4. | Gas Burner |
|  |  | a. Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve |

with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.	Burner Turndown - Turndown range shall be 7:1 when firing natural gas. c.	CO on Natural Gas is 25 ppm with excess air at 25%.

2.5	BOILER CONTROLS AND CONTROL PANEL

A.	Control Panel - shall be integral with the burner and shall contain a flame safeguard control, motor relays, and terminal strips mounted internally on a panel subbase. Lights, switches, and a control circuit breaker are mounted externally.

B.	Entrance Panel - high voltage panel shall be NEMA 4/12 rated and shall be mounted at the side of the boiler in a location convenient to the operator.

C.	CB780E Flame Safeguard - Each boiler shall be factory equipped with flame safeguard controller panel-mounted.

Oil, heat and moisture resistant wire shall be used and identified with circuit numbers corresponding to the electrical wiring diagram.

Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.

2.6	FLUE GAS HEAT RECOVERY (OPTIONAL SELECTION)

A.	Add Cleaver Brooks economizer selection in this area.

B.	Boiler and economizer to be designed with integral supports allowing for easy economizer installation on boiler eliminating the requirement for separate structure steel support.

2.7	EFFICIENCY GUARANTEE

A.	The boiler must be guaranteed to operate at a minimum fuel-to-water efficiency of

percent at 100% of rating when burning natural gas and

fuel-to-water efficiency at

100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).

PART 3 	EXECUTION

3.1	WARRANTY

A.	All equipment is to be guaranteed against defects in materials and/or workmanship for a period of 12 months from date of start-up, or 18 months from date of shipment; whichever comes first.

3.2	SHOP TESTS

A.	The packaged boiler must receive factory tests to check the construction, controls, and operation of the unit. All tests may be witnessed by the purchaser, if desired.

B.	Start-up Service

1.	After boiler installation is completed, the manufacturer shall provide the services of a field representative for starting the unit and training the operator at no additional costs.

2.	A factory-approved and authorized start-up report shall be submitted to the customer/user at the time of start-up.