May 22, 2012

Cleaver Brooks Elite Remote Monitoring and Data Logging Application Specifications

- Software

Package is based on Rockwell Automation Factory Talk SE Version 6.1 and includes

a. Factory Talk Site Addition Software

b. CB SCADA System Graphics and Data Package

- Hardware

Mini Tower computer system with:

a. Core 2 Dou E7500 with VT/2.93 Ghz, 3M 1066FSB processor

b. Microsoft Windows 7 Professional Operating System

c. 500GB SATA Hard Drive with 3 Gb/s and 16MB Data Burst Cache

d. 4 GB, Non-ECC, 1333 Mhz DDR3, 2X2GB Memory

e. 16X DVD+/RW SATA Only Drive

f. 256MB ATI RADEON HD 3450 Graphic Card

g. USB 101 Enhanced Keyboard

h. USB Optical Mouse

i. Speakers

- Options:

a. 9 pin Dot Matrix Alarm Logging Printer

b. Ink Jet Data Logging and Report Printer

c. 1000 VA Uninterruptable Power Supply

- Functionality

System must be able to be customized by Cleaver Brooks authorized personnel to meet reviewed and quoted functions outside the standard features defined below.

Data displayed, logged, and trended is described below, but is limited to the options selected and provided on the boiler, DA, surge tank, and master panel.

Application will provide displays as follows.

- Hawk Boiler control systems similar to Hawk boiler control operator interface,

- Provide overview display with boiler status, temperatures, pressures, water level and other boiler related information that reflect the options that the boiler is equipped with such as VFD, Parallel Positioning and O2 Trim.

- Provide burner management display that replicates the data and messages from the burner management device, CB780e or CB120e

- Provide firing rate screen display that shows the boiler on and off points, set point, process value, and current mode of operation

- Provide user analog input display that shows the instrumentation values connected to those inputs on each boiler, and reads in the current and totalized values.

- Provide trends for each boiler including process values such as stack temperature, pressure, water level, and firing rate. Trending must provide historical values limited to the data logs or operating system limits, but must be a minimum of one month. Provide the ability for the trend currently displayed on screen to be printed.

  - Reports and data logging

Provide hourly, shift, daily, monthly, and annual reports that summarize fuel consumed and hours of runtime per fuel per boiler. Reports to be saved electronically to the local hard drive and be able to be retrieved from within the application and can be printed or emailed. Reports must be archived for a minimum of 5 years.

  - Alarms - Active

Provide a summary of all active alarms from all connected systems including those that are active but not acknowledged, active and acknowledged, and no longer active, but not yet acknowledged. Provide the ability for the operator to add comments to an alarm when they are being acknowledged.

  - Alarms – History

Provide a summary of all alarm events from all connected systems.

  - ADAC DA and Surge tank

Provide display that is similar to the operator interface(s) on the attached ADAC systems. Be able to populate data from either a duo tank or two single tank ADAC systems. The overview display will provide tank level, tank temperature, tank pressure, common pump discharge header pressure, number of pumps, status of each pump and lead-lag order of the pumps,

  - Alarms - Active

Provide a summary of all active alarms from all connected systems including those that are active but not acknowledged, active and acknowledged, and no longer active, but not yet acknowledged. Provide the ability for the operator to add comments to an alarm when they are being acknowledged.

  - Alarms – History

Provide a summary of all alarm events from all connected systems.

- Provide displays similar to the Hawk Master Panel with the ability to read and write select data points as detailed below for a maximum of 8 boilers.

- For each boiler, boiler on and off point, lead lag sequence.

- System header pressure(steam systems) temperature(hot water systems)

- Lead boiler on off points

.

  - Alarms - Active

Provide a summary of all active alarms from all connected systems including those that are active but not acknowledged, active and acknowledged, and no longer active, but not yet acknowledged. Provide the ability for the operator to add comments to an alarm when they are being acknowledged.

  - Alarms – History

Provide a summary of all alarm events from all connected systems.

- Security

Provide a minimum of two levels of security which require user name and password to access. First level is operator security level which allows access to all standard functions. Second level is for factory only which allows access to configuration screens and shutdown.

- System must be configured and tested by factory trained and authorized personnel.

- Provide minimum of 1 day (8 hours) on-site training for customer personnel.

- Provide optional alarm printer, Dot matrix, for printing alarm events line by line

- Provide optional report printer, ink jet, for printing data reports, trend screens and screen captures.

- Provide UPS sized to maintain power to PC and display for minimum of 20 minutes.